## Slide 3
Pipes that connect to the compressor outside
Pipe to water drain
11inches between raised floor and cement foundation

## Slide 4
11in
Connector pipes

## Slide 5
Condenser
Connector pipes contained within wood box

## Slide 6
Wire size from power panel at generator is #6 to disconnect on Main Lab
Wire size from disconnect to machine is #8
Breaker size at power panel is 70 amp
Disconnect on Main Lab is 60 amp fused