## Slide 3
Pipes that connect to the compressor outside
Pipe to water drain
11inches between raised floor and cement foundation

## Slide 4
11in
Connector pipes

## Slide 5
Condenser
Connector pipes contained within wood box

## Slide 6
Wire size from power panel at generator is #6 to disconnect on Main Lab
Wire size from disconnect to machine is #8
Breaker size at power panel is 70 amp
Disconnect on Main Lab is 60 amp fused
Circuit breaker main distribution panel,
approx. 60ft to the right of condenser unit. Wire Size #6
Circuit breaker outside SPR approx. 6 ft left of condenser unit (60A)
Wire Size in #6 Wire Size out #8

## Slide 7
Location of Main Power distribution for HCRO
~30ft

## Slide 8
Wire size from power panel at generator is #6 to disconnect on Main Lab
Wire size from disconnect to machine is #8
Breaker size at power panel is 70 amp
Disconnect on Main Lab is 60 amp fused