## Slide 3
Pipes that connect to the compressor outside
Pipe to water drain
11inches between raised floor and cement foundation

## Slide 4
11in
Connector pipes

## Slide 5
Condenser
Connector pipes contained within wood box

## Slide 6
Wire size from power panel at generator is #6 to disconnect on Main Lab
Wire size from disconnect to machine is #8
Breaker size at power panel is 70 amp
Disconnect on Main Lab is 60 amp fused
Circuit breaker main distribution panel,
approx. 60ft to the right of condenser unit. Wire Size #6
Circuit breaker outside SPR approx. 6 ft left of condenser unit (60A)
Wire Size in #6 Wire Size out #8

## Slide 7
Location of Main Power distribution for HCRO
~30ft

## Slide 8
Wire size from power panel at generator is #6 to disconnect on Main Lab
Wire size from disconnect to machine is #8
Breaker size at power panel is 70 amp
Disconnect on Main Lab is 60 amp fused

## Slide 9
Location of Main Power distribution for HCRO
#6
existing wire
AC disconnect
new one required with 70A Fuse
#6
new wire (approx. 50ft)
Existing conduit is 3/4 in
New AC unit
SPR Main Power: spare circuit breaker for outside unit (460V 3phase)
#10
installation by HCRO
Connection to condenser
New condenser unit

## Slide 10
Location of Main Power replacement with 80A breaker
#4
new wire (approx. 150ft each)
total 450ft plus Ground
AC disconnect
new one required with 70A Fuse
#6
new wire (approx. 50ft each)
Existing conduit is 3/4 in
New AC unit
Condenser disconnect
Reuse of old panel 15A fuse
Connection to condenser
New condenser unit
#4
#12

## Slide 11
location for both disconnects,
inside unit and condenser