## Sheet1
Existing cooling capacity
Device:
HVAC |  |  | 10 | tons | 35.1685 | kW
AC1 |  |  | 4 | tons | 14.0674 | kW
AC2 |  |  | 4 | tons | 14.0674 | kW
[5 empty] | 63.3033 | kW
Current heat load
Device:
LO Rack | 1 | total | 1500 | W | 1.5 | kW
FW Rack | 1 | total | 2000 | W | 2 | kW
RFCB Rack | 1 | total | 1500 | W | 1.5 | kW
Array Control | 1 | each | 500 | W | 0.5 | kW
FRB-nodes | 6 | each | 600 | W | 3.6 | kW
SETI-nodes | 4 | each | 1300 | W | 5.2 | kW
Storage-node | 1 | each | 500 | W | 0.5 | kW
Obs-node | 1 | each | 600 | W | 0.6 | kW
Gnu-Radio | 2 | each | 600 | W | 1.2 | kW
Simulation-node | 1 | each | 500 | W | 0.5 | kW
Other-nodes | 4 | each | 250 | W | 1 | kW
Network Switches | 1 | total | 1000 | W | 1 | kW
SNAP | 12 | each | 50 | W | 0.6 | kW
IF Gain Control | 1 | each | 50 | W | 0.05 | kW
[5 empty] | 19.75 | kW
[5 empty] | 43.5533 | kW
Full build heat load
Device:
LO Rack | 1 | total | 1500 | W | 1.5 | kW
FW Rack | 1 | total | 2000 | W | 2 | kW
RFCB Rack | 1 | total | 1500 | W | 1.5 | kW
Array Control | 1 | each | 500 | W | 0.5 | kW
FRB-nodes | 6 | each | 600 | W | 3.6 | kW
SETI-nodes | 43 | each | 1300 | W | 55.9 | kW
Storage-node | 1 | each | 500 | W | 0.5 | kW
Obs-node | 1 | each | 600 | W | 0.6 | kW
Gnu-Radio | 2 | each | 600 | W | 1.2 | kW
Simulation-node | 1 | each | 500 | W | 0.5 | kW
Other-nodes | 4 | each | 250 | W | 1 | kW
Network Switches | 1 | total | 1000 | W | 1 | kW
SNAP | 12 | each | 50 | W | 0.6 | kW
IF Gain Control | 22 | each | 50 | W | 1.1 | kW
RFSoC | 21 | each | 180 | W | 3.78 | kW
[5 empty] | 75.28 | kW
[5 empty] | -11.9767 | kW